## NNC Details
NNC# | Location | Finding/ Description of Deficiency | Related Legal Reference(s) | Affected Program Owner
3 | Gas Plant ABC | On a routine Integrity Program site inspection of Gas Plant ABC, conducted 15 March 2015, NEB inspectors noted a condensate storage tank that appeared to be extensively rusted and asked the company to provide records of the last inspections as per API 653 for the Above Ground Storage Tank (AGST) #16-321. Company XYZ representatives on site were unable to provide the inspection records and were unable to ascertain whether the tank had ever been inspected. NEB Inspection Officer #1993 issued a Notice of Non-Compliance for this condensate storage tank. | OPR Section 40, CSA Z662-15, Clause 10.9.2.1, API 653 Section 6 - Inspection. | The Company XYZ representative that will be responsible for resolution of this NNC will be the Superintendent for Gas Plant ABC.
6 | Meter Station #2 | NEB inspectors were at Company XYZ's Meter Station #2 on 3 April 2015 to witness an excavation and repair of the below ground meter station piping. NEB inspectors noted that Company XYZ had a slop tank of approximately 10 cubic meters on site. NEB inspectors asked Company XYZ representatives to inquire with the Company Integrity Departement as to the most recent inspections (monthy, external and internal, as appropriate). Company representatives were unable to demonstrate that the above ground storage tank had been inspected as per the regulatory requirements. NEB Inspection Officer #1993 issued a Notice of Non-Compliance for this slop tank. | OPR Section 40, CSA Z662-15, Clause 10.9.2.1, API 653 Section 6 - Inspection. | The Company XYZ representative that will be responsible for resolution of this NNC will be the Area Director of Operations for the Northern Region.
9 | Compressor Station #3 | NEB inspectors were at Company XYZ's Compressor Station #3 on 15 April 2015 to conduct a routine inspection of the facility. NEB inspectors noted an above ground storage tank (AGST) on site, located on a raised earthen pad, that appeared to be excessively tilted. On returning to the area office, company representatives were able to provide the most recent API 653 external and internal inspection records, however, these records were not signed by an API 653 Authorized Inspector. NEB Inspection Officer #1993 issued a Notice of Non-Compliance for this AGST. | OPR Section 40, CSA Z662-15, Clause 10.9.2.1, API 653, Appendix D. | The Company XYZ representative that will be responsible for resolution of this NNC will be the Area Director of Operations for the Northern Region.
12 | Gas Plant XYZ | On a routine Integrity Program site inspection of Gas Plant XYZ, conducted 12 July 2015, NEB inspectors conducted a walk around of an AGST and noted that this tank had four external cathodic protection (CP) test stations and an impressed current CP rectifier. On closer inspection of the CP components, NEB inspectors noted that the rectifier was not operational at the time and that two of the test stations were in a state of disrepair (loose or disconnectied wires). Since it was not evident that the CP system was operational and that routine testing of the CP pipe to soil potentials may not have been conducted, NEB Inspection Officer #1993 issued a Notice of Non-Compliance for this AGST. | OPR Section 40, CSA Z662-15, Clause 10.9.2.1, API 651. | The Company XYZ representative that will be responsible for resolution of this NNC will be the Superintendent for Gas Plant XYZ.

## Analysis
NNC# | Location | Immediate/ Direct Cause(s) | Basic / Root Cause(s) | Related Schedule "A" requirement(s) | Corrective Action(s) | Preventative Action(s) | Describe how the proposed CAPAs addresses the deficiency(ies) | Summary of CAPA(s) / Desired End Result (DER)
#1 | Gas Plant ABC | Substandard Acts: Failure to follow procedures or practices. | Inadequate inspection and/or monitoring. | Element v.: Establishing and implementing a process for inspecting and monitoring company XYZ's activities and facilities and for taking corrective and preventive actions if deficiencies are identified. | Company XYZ will review all of its inspection records for the identified condensate tank at Gas Plant ABC to ascertain whether inspections had been conducted as per API 653. If the records indicate that the appropriate inspections have been conducted, Company XYZ will provide the complete records to the NEB to verify compliance with API 653. If the records indicate that the appropriate inspections have not been conducted, then Company XYZ will immediately schedule the required inspections and provide evidence to the NEB. | Company XYZ will review the inventory of all of its AGSTs for Gas Plants, meter staions and compressor stations and ensure that it has a complete and accurate compilation along with the inspection histories. Company XYZ will examine the inspection data and ensure that every AGST is in compliance with the requirements of API 653. If any AGSTs are found to be deficient in the required inspections, Company XYZ will immediately schedule the inspections and ensure that they are carried out in an expedient manner. | The Corrective Action will either serve to locate the records of the API 653 inspections, if they exist or undertake to have the inspections conducted if the tank had not been inspected previously. The Preventative Action will ensure that the company has a complete, accurate and up to date inventory of its AGSTs along with the records of past inspections. This will ensure that all AGSTs within the asset inventory of Company XYZ have been, or will be inspected per API 653 and be in compliance with the legal requirements. | Obtain records of inspection if done. Perform inspections if required. Complete an inventory of all AGSTs. Ensure all AGSTs have been or will be inspected as per the regulations. The overall DER is to ensure that all AGSTs in the asset inventory for the Company meet the regulatory requirements in terms of being inspected and the records exist as evidence of the inspections.
|  | Substandard Conditions: Inadequate information or data. |  | Element q.: Establishing and implementing a process for generating, retaining records that document the implementation of the management system and for providing access to those who require them in the course of their duties. | Company XYZ will critically review its records management system as it pertains to the generation and retention of records for its AGST inspections as per API 653. Company XYZ will identify all deficiencies and implement changes to its records management system as are required. | Company XYZ will, by having a records management system that is complete, accurate and up to date, ensure that it has all records of the inspections that are required by API 653. | Ensuring that Company XYZ has a records management system that includes all relevant and necessary records of inspection, monitoring and maintenance of its AGSTs as per API 653 will prevent similar occurrences of this non-compliance for all assets. | The DER is to have a complete, accurate and fully functional records management system as it applies to all of the Company's AGSTs.
|  |  | Inadequate awareness and communication of safety / health / regulations or guidelines. | Element h.: Establishing and implementing a process for identifying and monitoring compliance with all legal requirements that are applicable to Company XYZ in matters of safety, security and protection of the environment. | Company XYZ will critically review its process for identifying the legal requirements with respect to the inspection, monitoring and maintenance of its AGSTs as required by OPR 99, CSA Z662-15 and API 653. | Company XYZ will ensure that all of the applicable legal requirements and industry standards have been incorporated into its Operations and Maintenance Manual, Standard Operating Practices and any other relevant Work Scheduling processes for its AGST inspections as per API 653. | Ensuring that Company XYZ has identified all applicable legal requirements and industry standards as well as ensuring that these requirements have been included in its operating practices and procedures will prevent similar occurrences of this non-compliance for all of its AGTS assets. | The DER is to have identified all of the legal requirements and industry standards for AGSTs and to have incorporated these requirements into the Company's work processes and procedures.
|  |  | Inadequate communication of standards or regulations. | Element n.: Establishing and implementing a process for internal and external communication of information relating to safety, security and protection of the environment. | Company XYZ will critically review its communication processes and procedures as they apply to ensuring that its employees and contractors are aware of and understand the legal requirements with respect to the inspection, monitoring and maintenance of its AGSTs. | Company XYZ will identify gaps in its communication processes and procedures that have contributed to the lack of awareness and understanding of the legal requirements of the inspection requirements of its AGSTs and implement changes to address these gaps. | Company XYZ will have a fully developed and implemented communication process and this process will have been fully applied to all aspects of the inspection, monitoring and maintenance of the AGSTs. | The DER is to have a developed, established and implemented communciations process as it relates to all requirements of the Company's AGSTs.

## CAP Schedule
Quarterly Deliverables/ Commitments (to be filed for approval) | Date of filing | Target date for CAP Completion | Rationale for CAP Schedule